## notes
PLEASE PUT NOTES HERE OR USING COMMENT
| Nitrate-nitrogen (mg/l NO3-N ) | Nitrite-nitrogen (mg/l NO2-N) | E. coli (MPN/100ml) | Total Coliform (MPN/100ml) | Residual Chlorine (mg/l) | Fluoride (mg/l) | Arsenic (mg/l) | pH | EC (μS/cm) | Turbidity (NTU)
WHO guideline: | 11.3 mg/l NO3-N (50 mg/l NO3) | 0.0912 mg/l NO2-N; 3 mg/l NO2 | 0 CFU/100ml | 0 CFU/100ml | Max: 5 mg/l, residual chlorine > 0.5 mg/l after 30 minutes contact time, minimum at point of delivery: 0.2 mg/l | 1.5 mg/l | 0,01 mg/l | n/a | 1500 μS/cm | 5 NTU

## registration¦Registration Water
Submission Date | datapoint | #location | #lat | #lon | #water_source | #water_tech | #photo | #status
2021-01-04 | 1 | MLI.7.5_1 | 12.8621 | -5.204 | Borehole | Mechanized Pump | https://akvoflow-110.s3.amazonaws.com/images/413240ec-c65d-4c5c-bcc0-1aa52f79c5c3.jpg | Compliant
2021-01-04 | 2 | MLI.5.5_1 | 13.2312 | -7.7977 | Hand dug well - handpump | Handpump | https://akvoflow-110.s3.amazonaws.com/images/ba1b8f4d-dd0b-4bf7-b7fc-996903e76929.jpg | Non-compliant
2021-01-04 | 3 | MLI.5.5_1 | 13.9455 | -8.1666 | Hand dug well | Handpump | https://akvoflow-110.s3.amazonaws.com/images/5dd13126-64cc-43a6-a43d-5743f4935215.jpg | Compliant
2021-01-04 | 4 | MLI.6.5_1 | 13.7922 | -3.1876 | Borehole | Mechanized Pump | https://api.mwater.co/v3/images/5411c107d11e409f8d81bb1690cd3e9b | Compliant
2021-01-04 | 5 | MLI.5.5_1 | 13.1308 | -8 | Hand dug well | Handpump | https://akvoflow-110.s3.amazonaws.com/images/6977d849-5934-494e-b11e-577d1360d5a9.jpg | Compliant
2021-01-04 | 6 | MLI.5.5_1 | 13.1485 | -7.9481 | Borehole | Handpump | https://akvoflow-110.s3.amazonaws.com/images/ad69c2d3-b3e7-4a9b-bcca-3625fa00ba48.jpg | Compliant
2021-01-05 | 7 | MLI.6.2_1 | 13.6868 | -3.4796 | Borehole | Mechanized Pump | https://akvoflow-110.s3.amazonaws.com/images/0049170e-b1de-4305-9dcd-cb86a25a2286.jpg | Compliant
2021-01-05 | 8 | MLI.7.5_1 | 12.828 | -5.1321 | Borehole | Submersible Pump | https://akvoflow-110.s3.amazonaws.com/images/1503c1fd-da6a-4c7f-bdec-8ee13e666192.jpg | Compliant
2021-01-06 | 9 | MLI.7.7_1 | 13.589 | -4.5274 | Spring box |  | https://akvoflow-110.s3.amazonaws.com/images/ce18c4db-60ab-4021-8b11-f23c8c244196.jpg | Compliant
2021-01-06 | 10 | MLI.5.5_1 | 13.6792 | -7.9354 | Hand dug well | Handpump | https://akvoflow-110.s3.amazonaws.com/images/3bf2eded-9d37-4aa6-b2cb-72a6334ec130.jpg | Compliant

## monitoring¦Water Quality Tests
Submission Date | datapoint | Nitrate-nitrogen (mg/l NO3-N ) | Nitrite-nitrogen (mg/l NO2-N) | E. coli (MPN/100ml) | Total Coliform (MPN/100ml) | Residual Chlorine (mg/l) | Fluoride (mg/l) | Arsenic (mg/l) | pH | EC (μS/cm) | Turbidity (NTU)
2021-01-01 | 2 | 2.8 | 0.05 | 0 | 0 | 0.68 | 0 | 0 | 7.3 | 304 | 0
2021-06-01 | 2 | 3.1 | 0.05 | 0 | 0 | 0.77 | 0 | 0 | 7.2 | 313 | 0
2022-01-01 | 2 | 2.9 | 0.06 | 0 | 0 | 0.63 | 0 | 0 | 7.3 | 258 | 0
2022-06-01 | 2 | 3 | 0.05 | 0 | 0 | 0.72 | 0 | 0 | 7.1 | 353 | 0
2023-01-01 | 2 | 3.1 | 0.05 | 0 | 0 | 0.84 | 0 | 0 | 7.3 | 278 | 0
2023-06-01 | 2 | 3.4 | 0.05 | 0 | 0 | 1.45 | 0 | 0 | 7.2 | 389 | 0
2024-01-01 | 2 | 4 | 0.06 | 0 | 0 | 0.73 | 0 | 0 | 7.3 | 341 | 0
2024-06-01 | 2 | 3.9 | 0.06 | 0 | 0 | 0.86 | 0 | 0 | 7 | 296 | 0
2025-01-01 | 2 | 4.3 | 0.07 | 0 | 0 | 0.93 | 0 | 0 | 6.8 | 328 | 0
2025-06-01 | 2 | 5 | 0.09 | 13.6 | 48.3 | 0.19 | 0 | 0 | 7 | 336 | 2.5

## monitoring¦Other Monitoring Act
Submission Date | datapoint | Is there a latrine or other source of fecal contamination uphill of the well? | Is there any source of other contamination within 10m of the well (e.g., animals, agriculture, cultivation, roads, industry)? | Are there discarded chemical containers (i.e. oil cans) | Is the well apron cracked or damaged? | Is the drainage channel absent or cracked? | Is the well apron and drainage channel clean? | Is there pooling water within the well apron? | Do you find any build up of algae, dirt and foul smell on the jerry can? | How many Jerry cans? | Is there a spike in diarrheal cases?
2021-01-01 | 2 | No | No | No | No cracks/damage | No cracks/damage | Yes | No | No |  | No
2021-06-01 | 2 | No | No | No | No cracks/damage | No cracks/damage | Yes | No | No |  | No
2022-01-01 | 2 | No | No | No | No cracks/damage | No cracks/damage | Yes | No | No |  | No
2022-06-01 | 2 | No | No | No | No cracks/damage | No cracks/damage | Yes | No | No |  | No
2023-01-01 | 2 | No | No | No | Small cracks/damage | Small cracks/damage | Yes | No | No |  | No
2023-06-01 | 2 | No | No | No | Small cracks/damage | Small cracks/damage | Yes | No | No |  | No
2024-01-01 | 2 | No | No | No | Small cracks/damage | Small cracks/damage | Yes | No | No |  | No
2024-06-01 | 2 | No | No | No | Medium cracks/damage | Medium cracks/damage | Yes | No | No |  | No
2025-01-01 | 2 | No | No | No | Medium cracks/damage | Medium cracks/damage | Yes | No | No |  | No
2025-06-01 | 2 | No | No | No | Medium cracks/damage | Medium cracks/damage | Yes | No | No |  | Yes

## non-compliance¦Non-Compliance
Submission Date | datapoint | Monitoring Acitivity | Item of Non-Compliance | Value | Standard Value | Status | Action Report Submitted | Date of Report
2025-06-01 | 2 | 3. WQ test of water directly from pump | E. coli (MPN/100ml) | 13.6 | Not higher than zero | Corrective Measures Taken | [file] | 2025-07-01
2025-06-01 | 2 | 3. WQ test of water directly from pump | Total Coliform (MPN/100ml) | 38.3 | Not higher than zero | Corrective Measures Taken | [file] | 2025-07-01
2025-06-01 | 2 | 5. WQ test of water after chlorine dosing | Residual Chlorine (mg/l) | 0.19 | <0.2 mg/L after dosing | Action Needed