## notes
PLEASE PUT NOTES HERE OR USING COMMENT
| Nitrate (mg/l NO3) | Nitrite (mg/l NO2) | E. coli (MPN/100ml) | Total Coliform (MPN/100ml) | Residual Chlorine (mg/l) | Fluoride (mg/l) | Arsenic (mg/l) | EC (μS/cm) | Turbidity (NTU)
WHO guideline: | 50 mg/l NO3 | 3 mg/l NO2 | 0 CFU/100ml | 0 CFU/100ml | Minimum at point of delivery: 0.2 mg/l (Max: 5 mg/l) | 1.5 mg/l | 0,01 mg/l | 1500 μS/cm | 5 NTU
Water contamination hazards and control measures
Hazard | Control measures
Animals or humans defecating within the zone of influence | Zone of influence is cleared marked with signs and fencing. Prevent any animals from entering and minimise human activity in the zone of influence. Local by-laws established to protect the zone of influence
Other hazardous substances dumped within the zone of influence | Forbid any activities that may lead to contamination of the aquifer, such as disposal of wastes. Construct a protective concrete apron around the handpump to prevent surface water from pooling at the pump.
Poor hygiene practices while collecting and transferring water | Construct a concrete pad at the hand pump to keep the area clean. Have an attendant add chlorine tablets to each water container at the hand pump after it is filled. The dosage will allow for adequate residual chlorine to protect against bacteriological contamination during transport and for a limited period while stored at home.
Water containers were not clean | WASH committee to sell jerry cans and bleach at affordable prices
Monitoring plan
Monitoring activity |  | Description and comments | Frequency | Who is responsible?
1 | Inspection of zone of influence for signs of contamination | For example, look for open defecation, presence of animals, and discarded chemical containers (i.e. oil cans). This is to confirm that controls 1, 2, 3 and 4 are being followed. | Monthly
2 | Inspect the hand pump and apron for damage | Look for cracks or gaps that may allow surface water to enter the borehole. This is to confirm that control 5 is still effective. | Daily
3 | WQ test of water pumped directly from pump | At the very least, test for Total and E. coliforms, but ideally test the full suite of parameters as the commissioning. This is to check if the controls 1 through 5 have somehow failed or were not sufficient. | Annually
4 | Inspect hygiene conditions at the hand pump | The concrete pad should be clean and not pooling water. This is to check for control 6. | Daily
5 | WQ test of water after chlorine dosing | Test for residual chlorine. This is to confirm that the dosing is done correctly (control 7). | Monthly
6 | Conduct a systematic inspection of jerry cans at the hand pump and within households | Look for build up of algae and dirt, and foul smell. This is to confirm whether control 8 is effective. | Monthly
7 | Surveillance of diarrheal rates | Look for spikes in diarrheal cases. This is to check if control measures were effective and sufficient | Continuous (WASH committee receives reports of cases)
8 | WQ test of water at households | Test for total and E. coli. This is to confirm whether controls 7 and 8 are effective and sufficient. | If a spike in diarrhea rates were found

## guides
question | value | rule | note
Nitrate (mg/l NO3) | 50
Nitrite (mg/l NO2) | 3
E. coli (MPN/100ml) | 0 | higher | (higher than 0 is red)
Total Coliform (MPN/100ml) | 0 | higher | (higher than 0 is red)
Residual Chlorine (mg/l) | 0.2 | lower | (lower than 0.2 is red)
Fluoride (mg/l) | 1.5
Arsenic (mg/l) | 0.01
EC (μS/cm) | 1500
Turbidity (NTU) | 5

## colors
table | question | option | color
monitoring¦Inspection of zone of influence for signs of contamination | Is there a latrine or other source of fecal contamination uphill of the well? | yes | red
monitoring¦Inspection of zone of influence for signs of contamination | Is there a latrine or other source of fecal contamination uphill of the well? | no | green
monitoring¦Inspection of zone of influence for signs of contamination | Is there any source of other contamination within 10m of the well (e.g., animals, agriculture, cultivation, roads, industry)? | yes | red
monitoring¦Inspection of zone of influence for signs of contamination | Is there any source of other contamination within 10m of the well (e.g., animals, agriculture, cultivation, roads, industry)? | no | green
monitoring¦Inspection of zone of influence for signs of contamination | Are there discarded chemical containers (i.e. oil cans) | yes | red
monitoring¦Inspection of zone of influence for signs of contamination | Are there discarded chemical containers (i.e. oil cans) | no | green
monitoring¦Inspect the hand pump and apron for damage | Is the well apron cracked or damaged? | No cracks/damage | green
monitoring¦Inspect the hand pump and apron for damage | Is the well apron cracked or damaged? | Small cracks/damage | red
monitoring¦Inspect the hand pump and apron for damage | Is the well apron cracked or damaged? | Medium cracks/damage | red
monitoring¦Inspect the hand pump and apron for damage | Is the well apron cracked or damaged? | High cracks/damage | red
monitoring¦Inspect the hand pump and apron for damage | Is the drainage channel absent or cracked? | No cracks/damage | green
monitoring¦Inspect the hand pump and apron for damage | Is the drainage channel absent or cracked? | Small cracks/damage | red
monitoring¦Inspect the hand pump and apron for damage | Is the drainage channel absent or cracked? | Medium cracks/damage | red
monitoring¦Inspect the hand pump and apron for damage | Is the drainage channel absent or cracked? | High cracks/damage | red
monitoring¦Inspect hygiene conditions at the hand pump | Is the well apron and drainage channel clean? | yes | green
monitoring¦Inspect hygiene conditions at the hand pump | Is the well apron and drainage channel clean? | no | red
monitoring¦Inspect hygiene conditions at the hand pump | Is there pooling water within the well apron? | yes | red
monitoring¦Inspect hygiene conditions at the hand pump | Is there pooling water within the well apron? | no | green
monitoring¦Conduct a systematic inspection of jerry cans at the hand pump and within households | Do you find any build up of algae, dirt and foul smell on the jerry can? | yes | red
monitoring¦Conduct a systematic inspection of jerry cans at the hand pump and within households | Do you find any build up of algae, dirt and foul smell on the jerry can? | no | green
monitoring¦Surveillance of diarrheal rates | Is there a spike in diarrheal cases? | yes | red
monitoring¦Surveillance of diarrheal rates | Is there a spike in diarrheal cases? | no | green

## registration¦Description
Submission Date | datapoint | #location | #lat | #lon | #water_source | #water_tech | #photo | #status
2017-01-01 | 1 | MLI.7.5_1 | 12.8621 | -5.204 | Borehole | Mechanized Pump | https://akvoflow-110.s3.amazonaws.com/images/413240ec-c65d-4c5c-bcc0-1aa52f79c5c3.jpg | Compliant
2017-01-01 | 2 | MLI.5.5_1 | 13.2312 | -7.7977 | Hand dug well - handpump | Handpump | https://akvoflow-110.s3.amazonaws.com/images/ba1b8f4d-dd0b-4bf7-b7fc-996903e76929.jpg | Non-compliant
2017-01-04 | 3 | MLI.5.5_1 | 13.9455 | -8.1666 | Hand dug well | Handpump | https://akvoflow-110.s3.amazonaws.com/images/5dd13126-64cc-43a6-a43d-5743f4935215.jpg | Compliant
2017-01-01 | 4 | MLI.6.5_1 | 13.7922 | -3.1876 | Borehole | Mechanized Pump | https://api.mwater.co/v3/images/5411c107d11e409f8d81bb1690cd3e9b | Compliant
2017-01-04 | 5 | MLI.5.5_1 | 13.1308 | -8 | Hand dug well | Handpump | https://akvoflow-110.s3.amazonaws.com/images/6977d849-5934-494e-b11e-577d1360d5a9.jpg | Compliant
2017-01-04 | 6 | MLI.5.5_1 | 13.1485 | -7.9481 | Borehole | Handpump | https://akvoflow-110.s3.amazonaws.com/images/ad69c2d3-b3e7-4a9b-bcca-3625fa00ba48.jpg | Compliant
2017-01-05 | 7 | MLI.6.2_1 | 13.6868 | -3.4796 | Borehole | Mechanized Pump | https://akvoflow-110.s3.amazonaws.com/images/0049170e-b1de-4305-9dcd-cb86a25a2286.jpg | Compliant
2017-01-05 | 8 | MLI.7.5_1 | 12.828 | -5.1321 | Borehole | Submersible Pump | https://akvoflow-110.s3.amazonaws.com/images/1503c1fd-da6a-4c7f-bdec-8ee13e666192.jpg | Compliant
2017-01-06 | 9 | MLI.7.7_1 | 13.589 | -4.5274 | Spring box |  | https://akvoflow-110.s3.amazonaws.com/images/ce18c4db-60ab-4021-8b11-f23c8c244196.jpg | Compliant
2017-01-06 | 10 | MLI.5.5_1 | 13.6792 | -7.9354 | Hand dug well | Handpump | https://akvoflow-110.s3.amazonaws.com/images/3bf2eded-9d37-4aa6-b2cb-72a6334ec130.jpg | Compliant

## monitoring¦Inspection of zone o
Submission Date | datapoint | Is there a latrine or other source of fecal contamination uphill of the well? | Is there any source of other contamination within 10m of the well (e.g., animals, agriculture, cultivation, roads, industry)? | Are there discarded chemical containers (i.e. oil cans)
2020-09-01 | 2 | No | No | No
2020-10-01 | 2 | No | No | No
2020-11-01 | 2 | No | No | No
2020-12-01 | 2 | No | No | No
2021-01-01 | 2 | No | No | No
2021-02-01 | 2 | No | No | No
2021-03-01 | 2 | No | No | No
2021-04-01 | 2 | No | No | No
2021-05-01 | 2 | No | No | No
2021-06-01 | 2 | No | No | No

## monitoring¦Inspect the hand pum
Submission Date | datapoint | Is the well apron cracked or damaged? | Is the drainage channel absent or cracked?
2020-09-01 | 2 | No cracks/damage | No cracks/damage
2020-10-01 | 2 | No cracks/damage | No cracks/damage
2020-11-01 | 2 | No cracks/damage | No cracks/damage
2020-12-01 | 2 | No cracks/damage | No cracks/damage
2021-01-01 | 2 | Small cracks/damage | Small cracks/damage
2021-02-01 | 2 | Small cracks/damage | Small cracks/damage
2021-03-01 | 2 | Small cracks/damage | Small cracks/damage
2021-04-01 | 2 | Medium cracks/damage | Medium cracks/damage
2021-05-01 | 2 | Medium cracks/damage | Medium cracks/damage
2021-06-01 | 2 | Medium cracks/damage | Medium cracks/damage

## monitoring¦WQ test of water pum
Submission Date | datapoint | Nitrate (mg/l NO3) | Nitrite (mg/l NO2) | E. coli (MPN/100ml) | Total Coliform (MPN/100ml) | Residual Chlorine (mg/l) | Fluoride (mg/l) | Arsenic (mg/l) | pH | EC (μS/cm) | Turbidity (NTU)
2017-01-01 | 2 | 14 | 0.33 | 0 | 0 | 0.68 | 0 | 0 | 7.3 | 304 | 0
2017-06-01 | 2 | 15.5 | 0.35 | 0 | 0 | 0.77 | 0 | 0 | 7.2 | 313 | 0
2018-01-01 | 2 | 14.5 | 0.34 | 0 | 0 | 0.63 | 0 | 0 | 7.3 | 258 | 0
2018-06-01 | 2 | 15 | 0.34 | 0 | 0 | 0.72 | 0 | 0 | 7.1 | 353 | 0
2019-01-01 | 2 | 15.5 | 0.36 | 0 | 0 | 0.84 | 0 | 0 | 7.3 | 278 | 0
2019-06-01 | 2 | 17 | 0.38 | 0 | 0 | 1.45 | 0 | 0 | 7.2 | 389 | 0
2020-01-01 | 2 | 20 | 0.41 | 0 | 0 | 0.73 | 0 | 0 | 7.3 | 341 | 0
2020-06-01 | 2 | 19.5 | 0.4 | 0 | 0 | 0.86 | 0 | 0 | 7 | 296 | 0
2021-01-01 | 2 | 21.5 | 0.42 | 0 | 0 | 0.93 | 0 | 0 | 6.8 | 328 | 0
2021-06-01 | 2 | 25 | 0.47 | 13.6 | 48.3 | 0.19 | 0 | 0 | 7 | 336 | 2.5
2017-01-01 | 4 | 14 | 0.35 | 0 | 0 | 0.68 | 0 | 0 | 7.3 | 304 | 0
2017-06-01 | 4 | 15.5 | 0.37 | 0 | 0 | 0.77 | 0 | 0 | 7.2 | 313 | 0
2018-01-01 | 4 | 14.5 | 0.35 | 0 | 0 | 0.63 | 0 | 0 | 7.3 | 258 | 0
2018-06-01 | 4 | 15 | 0.36 | 0 | 0 | 0.72 | 0 | 0 | 7.1 | 353 | 0
2019-01-01 | 4 | 15.5 | 0.37 | 0 | 0 | 0.84 | 0 | 0 | 7.3 | 278 | 0
2019-06-01 | 4 | 17 | 0.39 | 0 | 0 | 1.45 | 0 | 0 | 7.2 | 389 | 0
2020-01-01 | 4 | 20 | 0.42 | 0 | 0 | 0.73 | 0 | 0 | 7.3 | 341 | 0
2020-06-01 | 4 | 19.5 | 0.4 | 0 | 0 | 0.86 | 0 | 0 | 7 | 296 | 0
2021-01-01 | 4 | 21.5 | 0.44 | 0 | 0 | 0.93 | 0 | 0 | 6.8 | 328 | 0
2021-06-01 | 4 | 25 | 0.51 | 13.6 | 48.3 | 0.19 | 0 | 0 | 7 | 336 | 2.5

## monitoring¦Inspect hygiene cond
Submission Date | datapoint | Is the well apron and drainage channel clean? | Is there pooling water within the well apron?
2020-09-01 | 2 | Yes | No
2020-10-01 | 2 | Yes | No
2020-11-01 | 2 | Yes | No
2020-12-01 | 2 | Yes | No
2021-01-01 | 2 | Yes | No
2021-02-01 | 2 | Yes | No
2021-03-01 | 2 | Yes | No
2021-04-01 | 2 | Yes | No
2021-05-01 | 2 | Yes | No
2021-06-01 | 2 | Yes | No

## monitoring¦WQ test of water aft
Submission Date | datapoint | Residual Chlorine (mg/l)
2020-09-01 | 2 | 0.68
2020-10-01 | 2 | 0.77
2020-11-01 | 2 | 0.63
2020-12-01 | 2 | 0.72
2021-01-01 | 2 | 0.84
2021-02-01 | 2 | 1.45
2021-03-01 | 2 | 0.73
2021-04-01 | 2 | 0.86
2021-05-01 | 2 | 0.93
2021-06-01 | 2 | 0.19
2020-09-01 | 4 | 0.68
2020-10-01 | 4 | 0.77
2020-11-01 | 4 | 0.63
2020-12-01 | 4 | 0.72
2021-01-01 | 4 | 0.84
2021-02-01 | 4 | 1.45
2021-03-01 | 4 | 0.73
2021-04-01 | 4 | 0.86
2021-05-01 | 4 | 0.93
2021-06-01 | 4 | 0.19

## monitoring¦Conduct a systematic
Submission Date | datapoint | Do you find any build up of algae, dirt and foul smell on the jerry can? | How many Jerry cans?
2020-09-01 | 2 | No
2020-10-01 | 2 | No
2020-11-01 | 2 | No
2020-12-01 | 2 | No
2021-01-01 | 2 | No
2021-02-01 | 2 | No
2021-03-01 | 2 | No
2021-04-01 | 2 | No
2021-05-01 | 2 | No
2021-06-01 | 2 | No

## monitoring¦Surveillance of diar
Submission Date | datapoint | Is there a spike in diarrheal cases?
2020-09-01 | 2 | No
2020-10-01 | 2 | No
2020-11-01 | 2 | No
2020-12-01 | 2 | No
2021-01-01 | 2 | No
2021-02-01 | 2 | No
2021-03-01 | 2 | No
2021-04-01 | 2 | No
2021-05-01 | 2 | No
2021-06-01 | 2 | Yes

## monitoring¦WQ test of water at
Submission Date | datapoint | E. coli (MPN/100ml) | Total Coliform (MPN/100ml)
2021-06-01 | 2 | 13.6 | 48.3

## non-compliance¦Non-Compliance
Submission Date | datapoint | Monitoring Acitivity | Item of Non-Compliance | Value | Standard Value | Status | Action Report Submitted | Date of Report
2021-06-01 | 2 | 3. WQ test of water directly from pump | E. coli (MPN/100ml) | 13.6 | Not higher than zero | Corrective Measures Taken | [file] | 2021-07-01
2021-06-01 | 2 | 3. WQ test of water directly from pump | Total Coliform (MPN/100ml) | 38.3 | Not higher than zero | Corrective Measures Taken | [file] | 2021-07-01
2021-06-01 | 2 | 5. WQ test of water after chlorine dosing | Residual Chlorine (mg/l) | 0.19 | <0.2 mg/L after dosing | Action Needed